/

Buffalo Air Handling Company

Field Startup Procedures

Check all foundations:  fan, isolation base and motor bolts for tightness.

Check set screws in the fan wheel for tightness to shaft.

Remove bearing caps on the bearings and check for proper grease.

Check for proper locking ring position in the held bearing.

Check that the free bearing is in the center of the running groove.

Check set screws in the bearings to insure bearing is locked.

Remove belt guard and check for sheave and belt alignment and proper tension.

Check all sheave and bushing hardware for tightness.

Check height of the isolation base to insure that base and isolators are level

Check to insure all shipping hold-down brackets have been removed.

Note following:   Motor HP ____________   Voltage ____________ FLA  _____________

Bump fan motor to check for proper wheel rotation.

Bring fan up to speed, checking for anything unusual like noise, vibration, pulsation, etc.

Check vibration levels on the fan bearings and motor bearings. Rebalance, if necessary.
 
  Check for any damage to the unit interior and exterior. Repair, if necessary
 
  Check all lights, doors, door handles / filter gauges for any damages. Repair, if necessary

  Check all coil fins for damage. Repair, if necessary

Check all dampers for proper movement and operation of the blades.

EQUIPMENT TAG NO._____________________________ BAH ORDER NO.______________________

PROJECT NAME: _____________________________________________________________________

STARTUP SUCCESSFULLY COMPLETED BY:_____________________________  DATE:___________

Buffalo Air Handling Company  467 Zane Snead Drive  Amherst, VA 24521  Tel:  804-946-7455 

Fax:  804-946-7941  www.buffaloair.com