Start-Up Procedures

Buffalo Air Handling Units

# Pre-Start Up Checklist and Service Request

Use this form to check for proper installation of Buffalo Air Handling units.  If prepaid start-up service was ordered as part of the Air Handling order, return this completed form to your local Buffalo Air Handling Sales Representative to schedule start-up.  If start-up service was not ordered, but is desired, contact your local Buffalo Air Handling Sales Representative for a quotation and then return this completed form with purchase order to schedule the start-up.  Please allow 3 – 4 weeks for start-up service.

| Job Name |  | Installing Contractor |  |
| --- | --- | --- | --- |
| Street |  | Contractor Contact |  |
| City |  | Phone |  |

## Pre-Start Up Checklist

Before attempting to start-up the Air Handling Unit, confirm that the following actions have been completed (or will be completed prior to scheduled start-up).  Refer to Buffalo Air Handling Service Manual G-875-F.

|  |  | YES | NO |
| --- | --- | --- | --- |
| 1. | Unit installed on Support structure, leveled and shimmed. |  |  |
| 2. | Proper assembly of unit and proper sealing of all shipping splits (welded or bolted) |  |  |
| 3. | If units supplied with inertia bases, has concrete been poured in base? |  |  |
| 4. | Release all shipping hold down devices. |  |  |
| 5. | Has ductwork been installed so fan can be run? |  |  |
| 6. | Check for proper clearance of all rotating components and adjust as required. |  |  |
| 7. | Check bearings for proper lubrication, cleanliness, moisture, alignment locking and clearances. |  |  |
| 8. | Align all drive components. |  |  |
| 9. | Check motor rotation. |  |  |
| 10. | Has power been brought to unit (fan, lights, etc.)? |  |  |
| 11. | Have filters been installed in units. |  |  |
| 12. | Are the VIV’s and damper operators operational? |  |  |
| 13. | Have VFD’s been started, checked and parameters set. Air balance and control done? |  |  |
| 14. | Has unit been cleaned out including coils and drain pans? |  |  |

Note: In the event service is purchased from Buffalo Air Handling, customer can disregard items 6, 7, and 8.  These will be done by Buffalo Air Handling service technician.

### REQUEST FOR SERVICE TECHNICIAN

I acknowledge that all of the above items have been completed.  I understand that if upon job inspection these requirements are not met, no start-up work will be performed and travel time and expenses will be charged at current hourly rates.

| Name: |  | Company |  | Date |  |
| --- | --- | --- | --- | --- | --- |