- Section 15XXX :  CORROSIVE EXHAUST DUCTWORK

PART 1	GENERAL

- 1.1	REFERENCES

SMACNA-01	Accepted Industry Practice for Industrial Duct Construction

SMACNA-06       HVAC Duct Construction Standards

SMACNA		   Round Industrial Duct Construction Standards

- Factory Mutual Research Standard 4922

- 1.2	DEFINITIONS

A.	Ductwork sizes on drawings state inside clear dimensions.

- 1.3	GENERAL REQUIREMENTS

A.		Fabricate ductwork in accordance with the latest edition of SMACNA Industrial 		Duct Construction Standards for both round and rectangular duct, unless more stringently 	detailed.

B.	Ductwork shall be listed for use as a fume and smoke exhaust duct without the 		need for an internal sprinkler protection system in accord with Factory Mutual Research 		Standard 4922.

- 1.4	QUALITY ASSURANCE

A.	Manufacturer shall be engaged in the regular and ongoing production of coated 		stainless steel ductwork and related components and accessories for a minimum of three 		years.

B.	Duct Manufacturer shall have current Factory Mutual (FM) listing verifying 		material meets FM 4922 requirements.

C.	Installer shall have a minimum of three years experience installing metal 			ductwork in industrial exhaust applications or systems.

- 1.5	SUBMITTALS

A.	Submit typical shop standards and/or SMACNA details for each class of duct 			specified, including particulars such as gauge sizes, welds, joint details and fitting 			configurations prior to start of work.

B.	Submit written report confirming ductwork has been fabricated and installed in 	  	accord with the latest SMACNA Standards and provisions of this specification.

C.	Submit shop drawings only when it is necessary to deviate from the intent of the 			design drawings.

D.	Submit product information as provided by the manufacturer.

PART 2	PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

A.	HALAR-ECTFE® Fluoropolymer coated stainless steel ductwork:

Kem-Tuff™ as manufactured by 	GDS Manufacturing

2 Chad Lane

Williston, VT  05495

B.	PTFE Joint Gasket											Kem-SeelTM				GDS Manufacturing						Kem-Flex SeelTM			Williston,    Vermont

C.	PTFE Expandable Gasket		W. L. Gore

Garlock

Intertec

2.2	MATERIALS

A.	ECTFE Fluoropolymer Coated Stainless Steel Ductwork

1.	Base metal shall be 300 Series stainless steel, with a 2-B exterior finish fabricated in accord with "SMACNA Round Industrial Duct Construction Standards" for the 				designated pressure classification. Unless otherwise specified ductwork gage and 			reinforcement will be based on Class 1, -6" WG schedule.

2.	The coating shall be HALAR-ECTFE fluopolymer, electrostatically applied 			powder coating system consisting of a primer and top coat. The coating shall be 			applied to provide complete and spark free coverage on the interior surface of 			ductwork and all components. An exterior coating may be applied for added 			protection in environments susceptible to corrosive attack.

B.	Companion Flange angle ring type Van Stone flanges shall be used for all 				component joints. Except between 4 inch and 12 inch use pressed 					flanges.Material of construction shall be 304 stainless steel. Flange dimensions 			and bolt pattern shall meet or exceed minimums prescribed in the SMACNA 			Round Industrial Duct construction Standards.

C.	Gaskets shall be used on all flanged joints. PTFE envelope type gaskets, .020" 			U-cut with a 1/8" neoprene filler, as supplied by GDS Manufacturing are 				recommended for round duct connections. Expanded PTFE gasket material may 			also be used at the owners discretion. Selection of appropriate type and sizing 			shall be per the manufacturer's recommendation.

D.	Support material shall be compatable with base material of duct construction, 			unless a liner is used to separate incompatible materials of construction.

2.3	DUCT CONSTRUCTION CLASSIFICATION

A.	Applications: Construct project duct systems in accordance with the following 			classifications schedule:

1.	Class 1 up to -6 inch WG; scrubbed exhaust

B.	Materials:	Use ECTFE fluoropolymer coated stainless steel pipe in 				construction ductwork for the scrubbed clean room exhaust systems.

PART 3	EXECUTION

3.1	FABRICATION

A.	No variation of duct configuration or sizes permitted except by written permission 	of the architect or design engineer.

B.	Use smooth non-gored elbows 4 inch thru 8 inch, where possible.

C.	Fabricate Tees, bends, and elbows with radius of not less than 1-1/2 times width 		of duct on centerline. Where rectangular elbows are used provide turning vanes. All 		mitered elbows shall have single thickness turning vanes; dual wall airfoil type blades are 	not acceptable.

D.	Drain and test port locations shall be determined prior to duct fabrication, and 		noted on detail drawings. Drain and test port configuration will be per Kem-Tuff 			standard unless otherwise noted.

E.	Increase duct sizes gradually, not exceeding a 15 degree divergence wherever 		possible. Maximum divergence upstream of equipment to be 30 degrees, and 45 degrees 		convergence downstream.

G.	Duct Fabrication:

1.	Longitudinal seams shall be fusion welded, no filler rod used.

2.	Transverse seams shall be continuous weld.

3.	All seams shall be ground clean and smooth.

- If additional reinforcement is required, submit proposal prior to bid for    HVAC system engineer's approval.

- Exterior of duct and fittings shall be free of any over spray

6.	Straight pipe fittings are fabricated in lengths per detail drawings..

F.	Manufacturer shall be certified by the coating manufacturer in the application of 		fluoropolymer coatings.

G.	Testing:	Each piece of  ductwork shall be spark tested over the entire 		coated surface area prior to shipment from the factory to insure a void free surface. A DC 		spark tester shall be used at 250 volts/mil setting.

3.2	INSTALLATION

A.	All Kem-Tuff Duct Products are to be installed per SMACNA specifications 		where applicable regarding but  not limited to location, support spacing, routing, and 		penetrations.

B.	Inspect each part on arrival for damage and notify GDS Manufacturing within 24 		hours of same.

C.	All Kem-Tuff ductwork is shipped with protective packaging, including end 		covers. Store ductwork with protective packaging in place. Storage area should be free of 		traffic and debris. Maintain protective packaging while handling ductwork at the work 		site. Remove protection just prior to installation.

D.	Clean ductwork prior to installation to remove dirt and dust. During installation 		close duct openings and open ends with temporary covers to prevent damage, and keep 		construction dust and debris from inside of duct.

E.	Install all supports in accordance with SMACNA Industrial Duct Construction 		Standards.

F.	Do not scratch, cut,  drill or penetrate the coating on the ductwork for any reason. 		All openings for drains, and testing or monitoring devices must be predetermined and 		factory installed.

G.	If coating is scratched or damaged once it has been received, contact the 			manufacturer for repair instructions. Repair kits are readily available and may be 			purchased from the manufacturer. All repairs must be spark tested prior to installation.

H.	Contractor shall conduct continuous random inspections during installation in 		accordance with the procedures outlined above.

I.	Align ductwork accurately at all connections to insure proper seal. Bolts for 		flanges shall be made from a material compatable with the base metal of the angle 		flange. Unless otherwise specified, for all duct greater than 4 inches in diameter, all bolts 		shall be 1/2" X 1-1/4". Torque bolts to 30 Ft-Lbs, then 25 Ft-Lbs in cross pattern. For 4 		inch diameter duct use 1/4” X 1-1/4” bolts, torqued to 10 Ft-Lbs then 8 Ft-Lbs in a cross 		pattern.

J.	Install slip joints only where absolutely necessary. All horizontal slip joints shall 		be pitched 1/8 inch per foot back to tool or nearest drain unless otherwise specified with 		outside end up. Use Kem-Tuff Slip Joint with Kem-FlexTM slip joint seal.

- END OF SECTION 15XXX